## AXA Heat
Preliminary Calculation of Prices & Dimensions
AB&CO Electrical Process Air Heaters
This calculation sheet is for determination of temperatures, flows and capacities,
- and finding a suitable AXA electrical air heater.
| Electrical heater, complete with elements, base plate and cable/terminal box - for side mounted | [8 empty] | 0
| in a gastight cabinet with flanges / counterflanges on air side. The cable connection box is raised | [9 empty] | 190.429 | 7
| 50 mm from base plate for cooling purposes. Industrial design, all parts arel made in stainless steel. | [8 empty] | 48.8237 | 239.2527 | 7
| Optimize your electrical air heater yourself. The secret is to keep the surface temperature (of the | [8 empty] | 48 | 1.02
electrical elements) as near 530°C as possible. Do not exceed 530°C, choose a lower load instead.
[14 empty] | 286.8129 |  |  | 1 |  | 22686.8786
| Mass Flow (kg/h) | 20000 | kg/h = | 44100 | lb/h | [8 empty] | 3.4364
| Air Inlet Temperature | 170 | °C = | 338 | °F
| Air outlet Temperature | 218 | °C = | 424.4 | °F
| Total Heat Capacity | 275.3404 | kW = | 938910.8604 | BTU/h
[10 empty] | 20 | 0.02337 | 0.001
| Optimizing to lowest price: | [8 empty] | 30 | 0.04241 | 0.001904
| Load of each element | 3.12 | kW = | 10639.2 | BTU/h |  |  |  |  | 40 | 0.07375 | 0.003134
| Surface temperature (<530°C) | 524.0465 | °C = | 975.2837 | °F
| Height (Face) | 1.1966 | m = | 3.926 | ft
| Width (Face) | 1.1966 | m = | 3.926 | ft
[10 empty] | 50 | 0.1234 | 0.004965
| Length (Overall) | 0.88 | m = | 2.8871 | ft |  |  |  |  | 60 | 0.1992 | 0.00758
| Budget Price (EXW) | 179587.6173 | DKK = | 24170.608 | EUR |  |  |  |  | 80 | 0.4736 | #REF!
[10 empty] | 90 | 0.7001 | 0.02265
| Delivery year | 2020
| If this solution seems to be attractive, and you would like to use this heater in your project, please | [8 empty] | 100 | 1.0133 | 0.03132
| contact our Sales & Projects Dept. for an exsact size and price. The above price is without acces- | [8 empty] | 110
| sories e.g. control panel, insulation with cover sheets, armatures and supporting legs. | [8 empty] | 120
Price is excluding VAT, duties and tax - based on delivery EXW Copenhagen.
NOTE: All above values are preliminary only, given without any responsibility for AB&CO.
AB&CO - TT BOILERS A/S ¦ Copenhagen, Denmark ¦ T: +45 4817 7599 W: www.abco.dk
1196.6372
1196.6372
3500
8.5
3.12
490
1
400
4
|  | 443 | 491
|  | 24951.127 | 27605.3273 | [5 empty] | 0.67436
|  | 0.80157 | 0.7245
|  | 1.0215 | 1.0293
|  | 0.67898 | 0.67436
|  | 0.68 | 0.7
|  | 3.0515e-05 | 3.6318e-05 | [5 empty] | 19.9399
|  | 0.0368 | 0.04016
|  | 3163.4809 | 2940.8157 |  |  |  |  | 0.67898
|  | 0.27 | 0.27 | [5 empty] | 31.6181
|  | 0.63 | 0.63
|  | 34.6517 | 33.0131 | [5 empty] | 37.3306
|  | 39.3545 | 37.3306
|  | 108.4686 | 112.2844 |  |  |  |  | 21.1222
|  | 316.8129 | 306.0465
|  | 486.8129 | 524.0465 |  |  |  |  | 32.8673
|  | 105.6043 | 102.0155 |  |  |  |  | 39.3545 |  |  |  |  | -50 | 1.57 | 1.007 | 0.0203 | 14.5 | 0.71
|  | 275.6043 | 320.0155 | [9 empty] | -40 | 1.4952 | 1.006 | 0.0215 | 15.1 | 0.7095
[13 empty] | -30 | 1.43 | 1.006 | 0.0222 | 15.5 | 0.709
|  | 490 | 490 | [9 empty] | -25 | 1.4 | 1.006 | 0.0226 | 15.8 | 0.71
|  | 7.2301 | 7.9992 | [9 empty] | -20 | 1.3765 | 1.006 | 0.023 | 16.15 | 0.71
[13 empty] | -19 | 1.3714 | 1.006 | 0.023075 | 16.1975 | 0.7095
[13 empty] | -18 | 1.3664 | 1.006 | 0.02315 | 16.245 | 0.709
|  | 8.5 | [10 empty] | -17 | 1.3613 | 1.006 | 0.023225 | 16.2925 | 0.7085
|  | 3500 | [10 empty] | -16 | 1.3563 | 1.006 | 0.0233 | 16.34 | 0.708
|  | 55685.2664 | [10 empty] | -15 | 1.3512 | 1.006 | 0.023375 | 16.3875 | 0.7075
|  | 1196.6372 | [10 empty] | -14 | 1.3462 | 1.006 | 0.02345 | 16.435 | 0.707
|  | 1196.6372 | [10 empty] | -13 | 1.3411 | 1.006 | 0.023525 | 16.4825 | 0.7065
|  | 958615.9012 | 0.66945 | [9 empty] | -12 | 1.3361 | 1.006 | 0.0236 | 16.53 | 0.706
|  | 1431940.6656 | [10 empty] | -11 | 1.331 | 1.006 | 0.023675 | 16.5775 | 0.7055
|  | 46.927 | [10 empty] | -10 | 1.326 | 1.006 | 0.02375 | 16.625 | 0.705
|  | 99.4453 | [10 empty] | -9 | 1.3209 | 1.006 | 0.023825 | 16.6725 | 0.7045
|  | 1.9589 | 195.9% | [9 empty] | -8 | 1.3158 | 1.006 | 0.0239 | 16.72 | 0.704
[13 empty] | -7 | 1.3108 | 1.006 | 0.023975 | 16.7675 | 0.7035
[13 empty] | -6 | 1.3057 | 1.006 | 0.02405 | 16.815 | 0.703
[13 empty] | -5 | 1.3007 | 1.006 | 0.024125 | 16.8625 | 0.7025
[13 empty] | -4 | 1.2956 | 1.006 | 0.0242 | 16.91 | 0.702
[13 empty] | -3 | 1.2906 | 1.006 | 0.024275 | 16.9575 | 0.7015
[13 empty] | -2 | 1.2855 | 1.006 | 0.02435 | 17.005 | 0.701
[13 empty] | -1 | 1.2805 | 1.006 | 0.024425 | 17.0525 | 0.7005
[13 empty] | 0 | 1.2754 | 1.006 | 0.0245 | 17.1 | 0.7
[13 empty] | 1 | 1.271 | 1.0061 | 0.024575 | 17.144 | 0.7
[13 empty] | 2 | 1.2667 | 1.0061 | 0.02465 | 17.188 | 0.7
[13 empty] | 3 | 1.2623 | 1.0061 | 0.024725 | 17.232 | 0.7
[13 empty] | 4 | 1.2579 | 1.0062 | 0.0248 | 17.276 | 0.7
|  |  | 1 | [9 empty] | 5 | 1.2536 | 1.0063 | 0.024779 | 17.2757 | 0.7
[13 empty] | 6 | 1.2492 | 1.0063 | 0.02495 | 17.364 | 0.7
|  |  | 1 | [9 empty] | 7 | 1.2448 | 1.0063 | 0.025025 | 17.408 | 0.7
[13 empty] | 8 | 1.2405 | 1.0064 | 0.0251 | 17.452 | 0.7
[13 empty] | 9 | 1.2361 | 1.0065 | 0.025175 | 17.496 | 0.7
[13 empty] | 10 | 1.2317 | 1.0065 | 0.025154 | 17.4957 | 0.7
[13 empty] | 11 | 1.2274 | 1.0065 | 0.025325 | 17.584 | 0.7
[13 empty] | 12 | 1.223 | 1.0066 | 0.0254 | 17.628 | 0.7
[13 empty] | 13 | 1.2187 | 1.0067 | 0.025475 | 17.672 | 0.7
[13 empty] | 14 | 1.2143 | 1.0067 | 0.02555 | 17.716 | 0.7
[13 empty] | 15 | 1.2099 | 1.0067 | 0.025529 | 17.7157 | 0.7
|  | 91.9272 | 275.7817 | [9 empty] | 16 | 1.2056 | 1.0068 | 0.0257 | 17.804 | 0.7
|  | 4 | 4 | [9 empty] | 17 | 1.2012 | 1.0069 | 0.025775 | 17.848 | 0.7
|  | 3.12 | 1.04 | [9 empty] | 18 | 1.1968 | 1.0069 | 0.02585 | 17.892 | 0.7
|  | 3.4364 | 1.1455 | [9 empty] | 19 | 1.1925 | 1.0069 | 0.025925 | 17.936 | 0.7
[13 empty] | 20 | 1.1881 | 1.007 | 0.026 | 17.98 | 0.7
[13 empty] | 21 | 1.1843 | 1.0071 | 0.026075 | 18.0215 | 0.6995
|  | 286.8129 | 286.8129 | [9 empty] | 22 | 1.1805 | 1.0071 | 0.02615 | 18.063 | 0.699
|  | 4.1667 | 4.1667 | [9 empty] | 23 | 1.1767 | 1.0071 | 0.026225 | 18.1045 | 0.6985
[13 empty] | 24 | 1.1729 | 1.0072 | 0.0263 | 18.146 | 0.698
|  | 400 | 400 | [9 empty] | 25 | 1.1691 | 1.0072 | 0.026375 | 18.1875 | 0.6975
|  | 400 | 230.9401 | [9 empty] | 26 | 1.1653 | 1.0073 | 0.02645 | 18.229 | 0.697
[13 empty] | 27 | 1.1615 | 1.0073 | 0.026525 | 18.2705 | 0.6965
|  | 413.9788 | 413.9788 | [9 empty] | 28 | 1.1577 | 1.0074 | 0.0266 | 18.312 | 0.696
|  | 717.0324 | 1241.9365 | [9 empty] | 29 | 1.1539 | 1.0074 | 0.026675 | 18.3535 | 0.6955
[13 empty] | 30 | 1.1501 | 1.0075 | 0.02675 | 18.395 | 0.695
|  | NO | YES | [9 empty] | 31 | 1.1462 | 1.0075 | 0.026825 | 18.4365 | 0.6945
[13 empty] | 32 | 1.1424 | 1.0076 | 0.0269 | 18.478 | 0.694
[13 empty] | 33 | 1.1386 | 1.0076 | 0.026975 | 18.5195 | 0.6935
|  | 5-6 | 5-6 | [9 empty] | 34 | 1.1348 | 1.0077 | 0.02705 | 18.561 | 0.693
|  | 30.6424 | 91.9272 | [9 empty] | 35 | 1.131 | 1.0077 | 0.027125 | 18.6025 | 0.6925
|  | 9.36 | 3.12 | [9 empty] | 36 | 1.1272 | 1.0078 | 0.0272 | 18.644 | 0.692
|  | 286.8129 | 286.8129 | [9 empty] | 37 | 1.1234 | 1.0078 | 0.027275 | 18.6855 | 0.6915
[13 empty] | 38 | 1.1196 | 1.0079 | 0.02735 | 18.727 | 0.691
|  | 0 | 0 | [9 empty] | 39 | 1.1158 | 1.0079 | 0.027425 | 18.7685 | 0.6905
[13 empty] | 40 | 1.112 | 1.008 | 0.0275 | 18.81 | 0.69
|  | 0 | 0 | [9 empty] | 41 | 1.1087 | 1.008 | 0.02757 | 18.856 | 0.69
[13 empty] | 42 | 1.1053 | 1.0081 | 0.02764 | 18.902 | 0.69
[10 empty] | 162 | 2870 |  | 43 | 1.102 | 1.0082 | 0.02771 | 18.948 | 0.69
[13 empty] | 44 | 1.0986 | 1.0082 | 0.02778 | 18.994 | 0.69
[13 empty] | 45 | 1.0953 | 1.0082 | 0.02785 | 19.04 | 0.69
[13 empty] | 46 | 1.092 | 1.0083 | 0.02792 | 19.086 | 0.69
[13 empty] | 47 | 1.0886 | 1.0084 | 0.02799 | 19.132 | 0.69
[13 empty] | 48 | 1.0853 | 1.0084 | 0.02806 | 19.178 | 0.69
[13 empty] | 49 | 1.0819 | 1.0084 | 0.02813 | 19.224 | 0.69
[9 empty] | 6 |  |  |  | 50 | 1.0786 | 1.0085 | 0.0282 | 19.27 | 0.69
[13 empty] | 51 | 1.0753 | 1.0086 | 0.02827 | 19.316 | 0.69
[13 empty] | 52 | 1.0719 | 1.0086 | 0.02834 | 19.362 | 0.69
[13 empty] | 53 | 1.0686 | 1.0086 | 0.02841 | 19.408 | 0.69
[10 empty] | 166 | 2920 |  | 54 | 1.0652 | 1.0087 | 0.02848 | 19.454 | 0.69
[10 empty] | 170 | 2960 |  | 55 | 1.0619 | 1.0088 | 0.02855 | 19.5 | 0.69
[10 empty] | 175 | 3000 |  | 56 | 1.0586 | 1.0088 | 0.02862 | 19.546 | 0.69
[10 empty] | 181 | 3200 |  | 57 | 1.0552 | 1.0088 | 0.02869 | 19.592 | 0.69
[13 empty] | 58 | 1.0519 | 1.0089 | 0.02876 | 19.638 | 0.69
[9 empty] | 5-6 |  |  |  | 59 | 1.0485 | 1.009 | 0.02883 | 19.684 | 0.69
[13 empty] | 60 | 1.0452 | 1.009 | 0.0289 | 19.73 | 0.69
[9 empty] | 7 |  |  |  | 61 | 1.0422 | 1.0091 | 0.028975 | 19.78 | 0.69
[9 empty] | 8 |  |  |  | 62 | 1.0393 | 1.0091 | 0.02905 | 19.83 | 0.69
[9 empty] | 9 |  |  |  | 63 | 1.0363 | 1.0091 | 0.029125 | 19.88 | 0.69
[9 empty] | 10 |  |  |  | 64 | 1.0333 | 1.0092 | 0.0292 | 19.93 | 0.69
[6 empty] | 5-6 | 5-6 | 5-6 |  |  |  |  | 65 | 1.0304 | 1.0092 | 0.029275 | 19.98 | 0.69
[13 empty] | 66 | 1.0274 | 1.0093 | 0.02935 | 20.03 | 0.69
[13 empty] | 67 | 1.0244 | 1.0093 | 0.029425 | 20.08 | 0.69
[13 empty] | 68 | 1.0215 | 1.0094 | 0.0295 | 20.13 | 0.69
[13 empty] | 69 | 1.0185 | 1.0094 | 0.029575 | 20.18 | 0.69
[13 empty] | 70 | 1.0155 | 1.0095 | 0.02965 | 20.23 | 0.69
[13 empty] | 71 | 1.0126 | 1.0095 | 0.029725 | 20.28 | 0.69
[13 empty] | 72 | 1.0096 | 1.0096 | 0.0298 | 20.33 | 0.69
[13 empty] | 73 | 1.0067 | 1.0096 | 0.029875 | 20.38 | 0.69
[13 empty] | 74 | 1.0037 | 1.0097 | 0.02995 | 20.43 | 0.69
[13 empty] | 75 | 1.0007 | 1.0097 | 0.030025 | 20.48 | 0.69
[13 empty] | 76 | 0.99776 | 1.0098 | 0.0301 | 20.53 | 0.69
[13 empty] | 77 | 0.99479 | 1.0098 | 0.030175 | 20.58 | 0.69
[13 empty] | 78 | 0.99183 | 1.0099 | 0.03025 | 20.63 | 0.69
[13 empty] | 79 | 0.98886 | 1.0099 | 0.030325 | 20.68 | 0.69
[13 empty] | 80 | 0.9859 | 1.01 | 0.0304 | 20.73 | 0.69
[13 empty] | 81 | 0.98325 | 1.0101 | 0.03047 | 20.7735 | 0.69
[13 empty] | 82 | 0.9806 | 1.0102 | 0.03054 | 20.817 | 0.69
[13 empty] | 83 | 0.97795 | 1.0103 | 0.03061 | 20.8605 | 0.69
[13 empty] | 84 | 0.9753 | 1.0104 | 0.03068 | 20.904 | 0.69
[13 empty] | 85 | 0.97265 | 1.0105 | 0.03075 | 20.9475 | 0.69
[13 empty] | 86 | 0.97 | 1.0106 | 0.03082 | 20.991 | 0.69
[13 empty] | 87 | 0.96735 | 1.0107 | 0.03089 | 21.0345 | 0.69
[13 empty] | 88 | 0.9647 | 1.0108 | 0.03096 | 21.078 | 0.69
[13 empty] | 89 | 0.96205 | 1.0109 | 0.03103 | 21.1215 | 0.69
[13 empty] | 90 | 0.9594 | 1.011 | 0.0311 | 21.165 | 0.69
[13 empty] | 91 | 0.95675 | 1.0111 | 0.03117 | 21.2085 | 0.69
[13 empty] | 92 | 0.9541 | 1.0112 | 0.03124 | 21.252 | 0.69
[13 empty] | 93 | 0.95145 | 1.0113 | 0.03131 | 21.2955 | 0.69
[13 empty] | 94 | 0.9488 | 1.0114 | 0.03138 | 21.339 | 0.69
[13 empty] | 95 | 0.94615 | 1.0115 | 0.03145 | 21.3825 | 0.69
[13 empty] | 96 | 0.9435 | 1.0116 | 0.03152 | 21.426 | 0.69
[13 empty] | 97 | 0.94085 | 1.0117 | 0.03159 | 21.4695 | 0.69
[13 empty] | 98 | 0.9382 | 1.0118 | 0.03166 | 21.513 | 0.69
[13 empty] | 99 | 0.93555 | 1.0119 | 0.03173 | 21.5565 | 0.69
[13 empty] | 100 | 0.9329 | 1.012 | 0.0318 | 21.6 | 0.69
[13 empty] | 101 | 0.93052 | 1.0121 | 0.03187 | 21.6415 | 0.6895
[13 empty] | 102 | 0.92815 | 1.0122 | 0.03194 | 21.683 | 0.689
[13 empty] | 103 | 0.92577 | 1.0123 | 0.03201 | 21.7245 | 0.6885
[13 empty] | 104 | 0.9234 | 1.0124 | 0.03208 | 21.766 | 0.688
[13 empty] | 105 | 0.92102 | 1.0125 | 0.03215 | 21.8075 | 0.6875
[13 empty] | 106 | 0.91865 | 1.0126 | 0.03222 | 21.849 | 0.687
[13 empty] | 107 | 0.91627 | 1.0127 | 0.03229 | 21.8905 | 0.6865
[13 empty] | 108 | 0.9139 | 1.0128 | 0.03236 | 21.932 | 0.686
[13 empty] | 109 | 0.91152 | 1.0129 | 0.03243 | 21.9735 | 0.6855
[13 empty] | 110 | 0.90915 | 1.013 | 0.0325 | 22.015 | 0.685
[13 empty] | 111 | 0.90677 | 1.0131 | 0.03257 | 22.0565 | 0.6845
[13 empty] | 112 | 0.9044 | 1.0132 | 0.03264 | 22.098 | 0.684
[13 empty] | 113 | 0.90202 | 1.0133 | 0.03271 | 22.1395 | 0.6835
[13 empty] | 114 | 0.89965 | 1.0134 | 0.03278 | 22.181 | 0.683
[13 empty] | 115 | 0.89727 | 1.0135 | 0.03285 | 22.2225 | 0.6825
[13 empty] | 116 | 0.8949 | 1.0136 | 0.03292 | 22.264 | 0.682
[13 empty] | 117 | 0.89253 | 1.0137 | 0.03299 | 22.3055 | 0.6815
[13 empty] | 118 | 0.89015 | 1.0138 | 0.03306 | 22.347 | 0.681
[13 empty] | 119 | 0.88777 | 1.0139 | 0.03313 | 22.3885 | 0.6805
[13 empty] | 120 | 0.8854 | 1.014 | 0.0332 | 22.43 | 0.68
[13 empty] | 121 | 0.88326 | 1.0142 | 0.033275 | 22.468 | 0.68
[13 empty] | 122 | 0.88111 | 1.0143 | 0.03335 | 22.506 | 0.68
[13 empty] | 123 | 0.87896 | 1.0145 | 0.033425 | 22.544 | 0.68
[13 empty] | 124 | 0.87682 | 1.0146 | 0.0335 | 22.582 | 0.68
[13 empty] | 125 | 0.87467 | 1.0148 | 0.033575 | 22.62 | 0.68
[13 empty] | 126 | 0.87253 | 1.0149 | 0.03365 | 22.658 | 0.68
[13 empty] | 127 | 0.87038 | 1.0151 | 0.033725 | 22.696 | 0.68
[13 empty] | 128 | 0.86824 | 1.0152 | 0.0338 | 22.734 | 0.68
[13 empty] | 129 | 0.86609 | 1.0153 | 0.033875 | 22.772 | 0.68
[13 empty] | 130 | 0.86395 | 1.0155 | 0.03395 | 22.81 | 0.68
[13 empty] | 131 | 0.86181 | 1.0156 | 0.034025 | 22.848 | 0.68
[13 empty] | 132 | 0.85966 | 1.0158 | 0.0341 | 22.886 | 0.68
[13 empty] | 133 | 0.85752 | 1.0159 | 0.034175 | 22.924 | 0.68
[13 empty] | 134 | 0.85537 | 1.0161 | 0.03425 | 22.962 | 0.68
[13 empty] | 135 | 0.85323 | 1.0163 | 0.034325 | 23 | 0.68
[13 empty] | 136 | 0.85108 | 1.0164 | 0.0344 | 23.038 | 0.68
[13 empty] | 137 | 0.84893 | 1.0165 | 0.034475 | 23.076 | 0.68
[13 empty] | 138 | 0.84679 | 1.0167 | 0.03455 | 23.114 | 0.68
[13 empty] | 139 | 0.84464 | 1.0168 | 0.034625 | 23.152 | 0.68
[13 empty] | 140 | 0.8425 | 1.017 | 0.0347 | 23.19 | 0.68
[13 empty] | 141 | 0.84056 | 1.0171 | 0.03477 | 23.231 | 0.68
[13 empty] | 142 | 0.83861 | 1.0173 | 0.03484 | 23.272 | 0.68
[13 empty] | 143 | 0.83666 | 1.0174 | 0.03491 | 23.313 | 0.68
[13 empty] | 144 | 0.83472 | 1.0176 | 0.03498 | 23.354 | 0.68
[13 empty] | 145 | 0.83278 | 1.0177 | 0.03505 | 23.395 | 0.68
[13 empty] | 146 | 0.83083 | 1.0179 | 0.03512 | 23.436 | 0.68
[13 empty] | 147 | 0.82888 | 1.018 | 0.03519 | 23.477 | 0.68
[13 empty] | 148 | 0.82694 | 1.0182 | 0.03526 | 23.518 | 0.68
[13 empty] | 149 | 0.825 | 1.0183 | 0.03533 | 23.559 | 0.68
[13 empty] | 150 | 0.82305 | 1.0185 | 0.0354 | 23.6 | 0.68
[13 empty] | 151 | 0.8211 | 1.0187 | 0.03547 | 23.641 | 0.68
[13 empty] | 152 | 0.81916 | 1.0188 | 0.03554 | 23.682 | 0.68
[13 empty] | 153 | 0.81722 | 1.019 | 0.03561 | 23.723 | 0.68
[13 empty] | 154 | 0.81527 | 1.0191 | 0.03568 | 23.764 | 0.68
[13 empty] | 155 | 0.81332 | 1.0192 | 0.03575 | 23.805 | 0.68
[13 empty] | 156 | 0.81138 | 1.0194 | 0.03582 | 23.846 | 0.68
[13 empty] | 157 | 0.80944 | 1.0195 | 0.03589 | 23.887 | 0.68
[13 empty] | 158 | 0.80749 | 1.0197 | 0.03596 | 23.928 | 0.68
[13 empty] | 159 | 0.80554 | 1.0198 | 0.03603 | 23.969 | 0.68
[13 empty] | 160 | 0.8036 | 1.02 | 0.0361 | 24.01 | 0.68
[13 empty] | 161 | 0.80183 | 1.0202 | 0.03617 | 24.055 | 0.68
[13 empty] | 162 | 0.80005 | 1.0203 | 0.03624 | 24.1 | 0.68
[13 empty] | 163 | 0.79827 | 1.0205 | 0.03631 | 24.145 | 0.68
[13 empty] | 164 | 0.7965 | 1.0206 | 0.03638 | 24.19 | 0.68
[13 empty] | 165 | 0.79473 | 1.0208 | 0.03645 | 24.235 | 0.68
[13 empty] | 166 | 0.79295 | 1.0209 | 0.03652 | 24.28 | 0.68
[13 empty] | 167 | 0.79117 | 1.0211 | 0.03659 | 24.325 | 0.68
[13 empty] | 168 | 0.7894 | 1.0212 | 0.03666 | 24.37 | 0.68
[13 empty] | 169 | 0.78763 | 1.0213 | 0.03673 | 24.415 | 0.68
[13 empty] | 170 | 0.78585 | 1.0215 | 0.0368 | 24.46 | 0.68
[13 empty] | 171 | 0.78407 | 1.0216 | 0.03687 | 24.505 | 0.68
[13 empty] | 172 | 0.7823 | 1.0218 | 0.03694 | 24.55 | 0.68
[13 empty] | 173 | 0.78053 | 1.0219 | 0.03701 | 24.595 | 0.68
[13 empty] | 174 | 0.77875 | 1.0221 | 0.03708 | 24.64 | 0.68
[13 empty] | 175 | 0.77697 | 1.0222 | 0.03715 | 24.685 | 0.68
[13 empty] | 176 | 0.7752 | 1.0224 | 0.03722 | 24.73 | 0.68
[13 empty] | 177 | 0.77343 | 1.0225 | 0.03729 | 24.775 | 0.68
[13 empty] | 178 | 0.77165 | 1.0227 | 0.03736 | 24.82 | 0.68
[13 empty] | 179 | 0.76987 | 1.0228 | 0.03743 | 24.865 | 0.68
[13 empty] | 180 | 0.7681 | 1.023 | 0.0375 | 24.91 | 0.68
[13 empty] | 181 | 0.76648 | 1.0232 | 0.03757 | 24.9495 | 0.68
[13 empty] | 182 | 0.76485 | 1.0233 | 0.03764 | 24.989 | 0.68
[13 empty] | 183 | 0.76323 | 1.0234 | 0.03771 | 25.0285 | 0.68
[13 empty] | 184 | 0.7616 | 1.0236 | 0.03778 | 25.068 | 0.68
[13 empty] | 185 | 0.75998 | 1.0237 | 0.03785 | 25.1075 | 0.68
[13 empty] | 186 | 0.75835 | 1.0239 | 0.03792 | 25.147 | 0.68
[13 empty] | 187 | 0.75672 | 1.024 | 0.03799 | 25.1865 | 0.68
[13 empty] | 188 | 0.7551 | 1.0242 | 0.03806 | 25.226 | 0.68
[13 empty] | 189 | 0.75348 | 1.0243 | 0.03813 | 25.2655 | 0.68
[13 empty] | 190 | 0.75185 | 1.0245 | 0.0382 | 25.305 | 0.68
[13 empty] | 191 | 0.75023 | 1.0247 | 0.03827 | 25.3445 | 0.68
[13 empty] | 192 | 0.7486 | 1.0248 | 0.03834 | 25.384 | 0.68
[13 empty] | 193 | 0.74698 | 1.025 | 0.03841 | 25.4235 | 0.68
[13 empty] | 194 | 0.74535 | 1.0251 | 0.03848 | 25.463 | 0.68
[13 empty] | 195 | 0.74372 | 1.0252 | 0.03855 | 25.5025 | 0.68
[13 empty] | 196 | 0.7421 | 1.0254 | 0.03862 | 25.542 | 0.68
[13 empty] | 197 | 0.74047 | 1.0255 | 0.03869 | 25.5815 | 0.68
[13 empty] | 198 | 0.73885 | 1.0257 | 0.03876 | 25.621 | 0.68
[13 empty] | 199 | 0.73723 | 1.0258 | 0.03883 | 25.6605 | 0.68
[13 empty] | 200 | 0.7356 | 1.026 | 0.0389 | 25.7 | 0.68
[13 empty] | 201 | 0.73419 | 1.0262 | 0.03897 | 25.734 | 0.6798
[13 empty] | 202 | 0.73279 | 1.0264 | 0.03904 | 25.768 | 0.6796
[13 empty] | 203 | 0.73138 | 1.0265 | 0.03911 | 25.802 | 0.6794
[13 empty] | 204 | 0.72998 | 1.0267 | 0.03918 | 25.836 | 0.6792
[13 empty] | 205 | 0.72857 | 1.0269 | 0.03925 | 25.87 | 0.679
[13 empty] | 206 | 0.72716 | 1.0271 | 0.03932 | 25.904 | 0.6788
[13 empty] | 207 | 0.72576 | 1.0273 | 0.03939 | 25.938 | 0.6786
[13 empty] | 208 | 0.72435 | 1.0274 | 0.03946 | 25.972 | 0.6784
[13 empty] | 209 | 0.72295 | 1.0276 | 0.03953 | 26.006 | 0.6782
[13 empty] | 210 | 0.72154 | 1.0278 | 0.0396 | 26.04 | 0.678
[13 empty] | 211 | 0.72013 | 1.028 | 0.03967 | 26.074 | 0.6778
[13 empty] | 212 | 0.71873 | 1.0282 | 0.03974 | 26.108 | 0.6776
[13 empty] | 213 | 0.71732 | 1.0283 | 0.03981 | 26.142 | 0.6774
[13 empty] | 214 | 0.71592 | 1.0285 | 0.03988 | 26.176 | 0.6772
[13 empty] | 215 | 0.71451 | 1.0287 | 0.03995 | 26.21 | 0.677
[13 empty] | 216 | 0.7131 | 1.0289 | 0.04002 | 26.244 | 0.6768
[13 empty] | 217 | 0.7117 | 1.0291 | 0.04009 | 26.278 | 0.6766
[13 empty] | 218 | 0.71029 | 1.0292 | 0.04016 | 26.312 | 0.6764
[13 empty] | 219 | 0.70889 | 1.0294 | 0.04023 | 26.346 | 0.6762
[13 empty] | 220 | 0.70748 | 1.0296 | 0.0403 | 26.38 | 0.676
[13 empty] | 221 | 0.70607 | 1.0298 | 0.04037 | 26.414 | 0.6758
[13 empty] | 222 | 0.70467 | 1.03 | 0.04044 | 26.448 | 0.6756
[13 empty] | 223 | 0.70326 | 1.0301 | 0.04051 | 26.482 | 0.6754
[13 empty] | 224 | 0.70186 | 1.0303 | 0.04058 | 26.516 | 0.6752
[13 empty] | 225 | 0.70045 | 1.0305 | 0.04065 | 26.55 | 0.675
[13 empty] | 226 | 0.69904 | 1.0307 | 0.04072 | 26.584 | 0.6748
[13 empty] | 227 | 0.69764 | 1.0309 | 0.04079 | 26.618 | 0.6746
[13 empty] | 228 | 0.69623 | 1.031 | 0.04086 | 26.652 | 0.6744
[13 empty] | 229 | 0.69483 | 1.0312 | 0.04093 | 26.686 | 0.6742
[13 empty] | 230 | 0.69342 | 1.0314 | 0.041 | 26.72 | 0.674
[13 empty] | 231 | 0.69201 | 1.0316 | 0.04107 | 26.754 | 0.6738
[13 empty] | 232 | 0.69061 | 1.0318 | 0.04114 | 26.788 | 0.6736
[13 empty] | 233 | 0.6892 | 1.0319 | 0.04121 | 26.822 | 0.6734
[13 empty] | 234 | 0.6878 | 1.0321 | 0.04128 | 26.856 | 0.6732
[13 empty] | 235 | 0.68639 | 1.0323 | 0.04135 | 26.89 | 0.673
[13 empty] | 236 | 0.68498 | 1.0325 | 0.04142 | 26.924 | 0.6728
[13 empty] | 237 | 0.68358 | 1.0327 | 0.04149 | 26.958 | 0.6726
[13 empty] | 238 | 0.68217 | 1.0328 | 0.04156 | 26.992 | 0.6724
[13 empty] | 239 | 0.68077 | 1.033 | 0.04163 | 27.026 | 0.6722
[13 empty] | 240 | 0.67936 | 1.0332 | 0.0417 | 27.06 | 0.672
[13 empty] | 241 | 0.67795 | 1.0334 | 0.04177 | 27.094 | 0.6718
[13 empty] | 242 | 0.67655 | 1.0336 | 0.04184 | 27.128 | 0.6716
[13 empty] | 243 | 0.67514 | 1.0337 | 0.04191 | 27.162 | 0.6714
[13 empty] | 244 | 0.67374 | 1.0339 | 0.04198 | 27.196 | 0.6712
[13 empty] | 245 | 0.67233 | 1.0341 | 0.04205 | 27.23 | 0.671
[13 empty] | 246 | 0.67092 | 1.0343 | 0.04212 | 27.264 | 0.6708
[13 empty] | 247 | 0.66952 | 1.0345 | 0.04219 | 27.298 | 0.6706
[13 empty] | 248 | 0.66811 | 1.0346 | 0.04226 | 27.332 | 0.6704
[13 empty] | 249 | 0.66671 | 1.0348 | 0.04233 | 27.366 | 0.6702
[13 empty] | 250 | 0.6653 | 1.035 | 0.0424 | 27.4 | 0.67
[13 empty] | 251 | 0.66414 | 1.0352 | 0.04247 | 27.436 | 0.67
[13 empty] | 252 | 0.66298 | 1.0354 | 0.04254 | 27.472 | 0.67
[13 empty] | 253 | 0.66181 | 1.0357 | 0.04261 | 27.508 | 0.67
[13 empty] | 254 | 0.66065 | 1.0359 | 0.04268 | 27.544 | 0.67
[13 empty] | 255 | 0.65949 | 1.0361 | 0.04275 | 27.58 | 0.67
[13 empty] | 256 | 0.65833 | 1.0363 | 0.04282 | 27.616 | 0.67
[13 empty] | 257 | 0.65717 | 1.0365 | 0.04289 | 27.652 | 0.67
[13 empty] | 258 | 0.656 | 1.0368 | 0.04296 | 27.688 | 0.67
[13 empty] | 259 | 0.65484 | 1.037 | 0.04303 | 27.724 | 0.67
[13 empty] | 260 | 0.65368 | 1.0372 | 0.0431 | 27.76 | 0.67
[13 empty] | 261 | 0.65252 | 1.0374 | 0.04317 | 27.796 | 0.67
[13 empty] | 262 | 0.65136 | 1.0376 | 0.04324 | 27.832 | 0.67
[13 empty] | 263 | 0.65019 | 1.0379 | 0.04331 | 27.868 | 0.67
[13 empty] | 264 | 0.64903 | 1.0381 | 0.04338 | 27.904 | 0.67
[13 empty] | 265 | 0.64787 | 1.0383 | 0.04345 | 27.94 | 0.67
[13 empty] | 266 | 0.64671 | 1.0385 | 0.04352 | 27.976 | 0.67
[13 empty] | 267 | 0.64555 | 1.0387 | 0.04359 | 28.012 | 0.67
[13 empty] | 268 | 0.64438 | 1.039 | 0.04366 | 28.048 | 0.67
[13 empty] | 269 | 0.64322 | 1.0392 | 0.04373 | 28.084 | 0.67
[13 empty] | 270 | 0.64206 | 1.0394 | 0.0438 | 28.12 | 0.67
[13 empty] | 271 | 0.6409 | 1.0396 | 0.04387 | 28.156 | 0.67
[13 empty] | 272 | 0.63974 | 1.0398 | 0.04394 | 28.192 | 0.67
[13 empty] | 273 | 0.63857 | 1.0401 | 0.04401 | 28.228 | 0.67
[13 empty] | 274 | 0.63741 | 1.0403 | 0.04408 | 28.264 | 0.67
[13 empty] | 275 | 0.63625 | 1.0405 | 0.04415 | 28.3 | 0.67
[13 empty] | 276 | 0.63509 | 1.0407 | 0.04422 | 28.336 | 0.67
[13 empty] | 277 | 0.63393 | 1.0409 | 0.04429 | 28.372 | 0.67
[13 empty] | 278 | 0.63276 | 1.0412 | 0.04436 | 28.408 | 0.67
[13 empty] | 279 | 0.6316 | 1.0414 | 0.04443 | 28.444 | 0.67
[13 empty] | 280 | 0.63044 | 1.0416 | 0.0445 | 28.48 | 0.67
[13 empty] | 281 | 0.62928 | 1.0418 | 0.04457 | 28.516 | 0.67
[13 empty] | 282 | 0.62812 | 1.042 | 0.04464 | 28.552 | 0.67
[13 empty] | 283 | 0.62695 | 1.0423 | 0.04471 | 28.588 | 0.67
[13 empty] | 284 | 0.62579 | 1.0425 | 0.04478 | 28.624 | 0.67
[13 empty] | 285 | 0.62463 | 1.0427 | 0.04485 | 28.66 | 0.67
[13 empty] | 286 | 0.62347 | 1.0429 | 0.04492 | 28.696 | 0.67
[13 empty] | 287 | 0.62231 | 1.0431 | 0.04499 | 28.732 | 0.67
[13 empty] | 288 | 0.62114 | 1.0434 | 0.04506 | 28.768 | 0.67
[13 empty] | 289 | 0.61998 | 1.0436 | 0.04513 | 28.804 | 0.67
[13 empty] | 290 | 0.61882 | 1.0438 | 0.0452 | 28.84 | 0.67
[13 empty] | 291 | 0.61766 | 1.044 | 0.04527 | 28.876 | 0.67
[13 empty] | 292 | 0.6165 | 1.0442 | 0.04534 | 28.912 | 0.67
[13 empty] | 293 | 0.61533 | 1.0445 | 0.04541 | 28.948 | 0.67
[13 empty] | 294 | 0.61417 | 1.0447 | 0.04548 | 28.984 | 0.67
[13 empty] | 295 | 0.61301 | 1.0449 | 0.04555 | 29.02 | 0.67
[13 empty] | 296 | 0.61185 | 1.0451 | 0.04562 | 29.056 | 0.67
[13 empty] | 297 | 0.61069 | 1.0453 | 0.04569 | 29.092 | 0.67
[13 empty] | 298 | 0.60952 | 1.0456 | 0.04576 | 29.128 | 0.67
[13 empty] | 299 | 0.60836 | 1.0458 | 0.04583 | 29.164 | 0.67
[13 empty] | 300 | 0.6072 | 1.046 | 0.0459 | 29.2 | 0.67
[13 empty] | 301 | 0.60623 | 1.0462 | 0.045968 | 29.234 | 0.6698
[13 empty] | 302 | 0.60525 | 1.0464 | 0.046036 | 29.268 | 0.6696
[13 empty] | 303 | 0.60428 | 1.0467 | 0.046105 | 29.302 | 0.6694
[13 empty] | 304 | 0.6033 | 1.0469 | 0.046173 | 29.336 | 0.6692
[13 empty] | 305 | 0.60233 | 1.0471 | 0.046241 | 29.37 | 0.669
[13 empty] | 306 | 0.60136 | 1.0473 | 0.046309 | 29.404 | 0.6688
[13 empty] | 307 | 0.60038 | 1.0475 | 0.046377 | 29.438 | 0.6686
[13 empty] | 308 | 0.59941 | 1.0478 | 0.046446 | 29.472 | 0.6684
[13 empty] | 309 | 0.59843 | 1.048 | 0.046514 | 29.506 | 0.6682
[13 empty] | 310 | 0.59746 | 1.0482 | 0.046582 | 29.54 | 0.668
[13 empty] | 311 | 0.59649 | 1.0484 | 0.04665 | 29.574 | 0.6678
[13 empty] | 312 | 0.59551 | 1.0486 | 0.046718 | 29.608 | 0.6676
[13 empty] | 313 | 0.59454 | 1.0489 | 0.046787 | 29.642 | 0.6674
[13 empty] | 314 | 0.59356 | 1.0491 | 0.046855 | 29.676 | 0.6672
[13 empty] | 315 | 0.59259 | 1.0493 | 0.046923 | 29.71 | 0.667
[13 empty] | 316 | 0.59162 | 1.0495 | 0.046991 | 29.744 | 0.6668
[13 empty] | 317 | 0.59064 | 1.0497 | 0.047059 | 29.778 | 0.6666
[13 empty] | 318 | 0.58967 | 1.05 | 0.047128 | 29.812 | 0.6664
[13 empty] | 319 | 0.58869 | 1.0502 | 0.047196 | 29.846 | 0.6662
[13 empty] | 320 | 0.58772 | 1.0504 | 0.047264 | 29.88 | 0.666
[13 empty] | 321 | 0.58675 | 1.0506 | 0.047332 | 29.914 | 0.6658
[13 empty] | 322 | 0.58577 | 1.0508 | 0.0474 | 29.948 | 0.6656
[13 empty] | 323 | 0.5848 | 1.0511 | 0.047469 | 29.982 | 0.6654
[13 empty] | 324 | 0.58382 | 1.0513 | 0.047537 | 30.016 | 0.6652
[13 empty] | 325 | 0.58285 | 1.0515 | 0.047605 | 30.05 | 0.665
[13 empty] | 326 | 0.58188 | 1.0517 | 0.047673 | 30.084 | 0.6648
[13 empty] | 327 | 0.5809 | 1.0519 | 0.047741 | 30.118 | 0.6646
[13 empty] | 328 | 0.57993 | 1.0522 | 0.04781 | 30.152 | 0.6644
[13 empty] | 329 | 0.57895 | 1.0524 | 0.047878 | 30.186 | 0.6642
[13 empty] | 330 | 0.57798 | 1.0526 | 0.047946 | 30.22 | 0.664
[13 empty] | 331 | 0.57701 | 1.0528 | 0.048014 | 30.254 | 0.6638
[13 empty] | 332 | 0.57603 | 1.053 | 0.048082 | 30.288 | 0.6636
[13 empty] | 333 | 0.57506 | 1.0533 | 0.048151 | 30.322 | 0.6634
[13 empty] | 334 | 0.57408 | 1.0535 | 0.048219 | 30.356 | 0.6632
[13 empty] | 335 | 0.57311 | 1.0537 | 0.048287 | 30.39 | 0.663
[13 empty] | 336 | 0.57214 | 1.0539 | 0.048355 | 30.424 | 0.6628
[13 empty] | 337 | 0.57116 | 1.0541 | 0.048423 | 30.458 | 0.6626
[13 empty] | 338 | 0.57019 | 1.0544 | 0.048492 | 30.492 | 0.6624
[13 empty] | 339 | 0.56921 | 1.0546 | 0.04856 | 30.526 | 0.6622
[13 empty] | 340 | 0.56824 | 1.0548 | 0.048628 | 30.56 | 0.662
[13 empty] | 341 | 0.56727 | 1.055 | 0.048696 | 30.594 | 0.6618
[13 empty] | 342 | 0.56629 | 1.0552 | 0.048764 | 30.628 | 0.6616
[13 empty] | 343 | 0.56532 | 1.0555 | 0.048833 | 30.662 | 0.6614
[13 empty] | 344 | 0.56434 | 1.0557 | 0.048901 | 30.696 | 0.6612
[13 empty] | 345 | 0.56337 | 1.0559 | 0.048969 | 30.73 | 0.661
[13 empty] | 346 | 0.5624 | 1.0561 | 0.049037 | 30.764 | 0.6608
[13 empty] | 347 | 0.56142 | 1.0563 | 0.049105 | 30.798 | 0.6606
[13 empty] | 348 | 0.56045 | 1.0566 | 0.049174 | 30.832 | 0.6604
[13 empty] | 349 | 0.55947 | 1.0568 | 0.049242 | 30.866 | 0.6602
[13 empty] | 350 | 0.5585 | 1.057 | 0.04931 | 30.9 | 0.66
[13 empty] | 351 | 0.55767 | 1.0572 | 0.049375 | 30.933 | 0.66
[13 empty] | 352 | 0.55684 | 1.0575 | 0.04944 | 30.966 | 0.66
[13 empty] | 353 | 0.55601 | 1.0577 | 0.049506 | 30.999 | 0.66
[13 empty] | 354 | 0.55518 | 1.058 | 0.049571 | 31.032 | 0.66
[13 empty] | 355 | 0.55435 | 1.0582 | 0.049636 | 31.065 | 0.66
[13 empty] | 356 | 0.55352 | 1.0584 | 0.049701 | 31.098 | 0.66
[13 empty] | 357 | 0.55269 | 1.0587 | 0.049766 | 31.131 | 0.66
[13 empty] | 358 | 0.55186 | 1.0589 | 0.049832 | 31.164 | 0.66
[13 empty] | 359 | 0.55103 | 1.0592 | 0.049897 | 31.197 | 0.66
[13 empty] | 360 | 0.5502 | 1.0594 | 0.049962 | 31.23 | 0.66
[13 empty] | 361 | 0.54937 | 1.0596 | 0.050027 | 31.263 | 0.66
[13 empty] | 362 | 0.54854 | 1.0599 | 0.050092 | 31.296 | 0.66
[13 empty] | 363 | 0.54771 | 1.0601 | 0.050158 | 31.329 | 0.66
[13 empty] | 364 | 0.54688 | 1.0604 | 0.050223 | 31.362 | 0.66
[13 empty] | 365 | 0.54605 | 1.0606 | 0.050288 | 31.395 | 0.66
[13 empty] | 366 | 0.54522 | 1.0608 | 0.050353 | 31.428 | 0.66
[13 empty] | 367 | 0.54439 | 1.0611 | 0.050418 | 31.461 | 0.66
[13 empty] | 368 | 0.54356 | 1.0613 | 0.050484 | 31.494 | 0.66
[13 empty] | 369 | 0.54273 | 1.0616 | 0.050549 | 31.527 | 0.66
[13 empty] | 370 | 0.5419 | 1.0618 | 0.050614 | 31.56 | 0.66
[13 empty] | 371 | 0.54107 | 1.062 | 0.050679 | 31.593 | 0.66
[13 empty] | 372 | 0.54024 | 1.0623 | 0.050744 | 31.626 | 0.66
[13 empty] | 373 | 0.53941 | 1.0625 | 0.05081 | 31.659 | 0.66
[13 empty] | 374 | 0.53858 | 1.0628 | 0.050875 | 31.692 | 0.66
[13 empty] | 375 | 0.53775 | 1.063 | 0.05094 | 31.725 | 0.66
[13 empty] | 376 | 0.53692 | 1.0632 | 0.051005 | 31.758 | 0.66
[13 empty] | 377 | 0.53609 | 1.0635 | 0.05107 | 31.791 | 0.66
[13 empty] | 378 | 0.53526 | 1.0637 | 0.051136 | 31.824 | 0.66
[13 empty] | 379 | 0.53443 | 1.064 | 0.051201 | 31.857 | 0.66
[13 empty] | 380 | 0.5336 | 1.0642 | 0.051266 | 31.89 | 0.66
[13 empty] | 381 | 0.53277 | 1.0644 | 0.051331 | 31.923 | 0.66
[13 empty] | 382 | 0.53194 | 1.0647 | 0.051396 | 31.956 | 0.66
[13 empty] | 383 | 0.53111 | 1.0649 | 0.051462 | 31.989 | 0.66
[13 empty] | 384 | 0.53028 | 1.0652 | 0.051527 | 32.022 | 0.66
[13 empty] | 385 | 0.52945 | 1.0654 | 0.051592 | 32.055 | 0.66
[13 empty] | 386 | 0.52862 | 1.0656 | 0.051657 | 32.088 | 0.66
[13 empty] | 387 | 0.52779 | 1.0659 | 0.051722 | 32.121 | 0.66
[13 empty] | 388 | 0.52696 | 1.0661 | 0.051788 | 32.154 | 0.66
[13 empty] | 389 | 0.52613 | 1.0664 | 0.051853 | 32.187 | 0.66
[13 empty] | 390 | 0.5253 | 1.0666 | 0.051918 | 32.22 | 0.66
[13 empty] | 391 | 0.52447 | 1.0668 | 0.051983 | 32.253 | 0.66
[13 empty] | 392 | 0.52364 | 1.0671 | 0.052048 | 32.286 | 0.66
[13 empty] | 393 | 0.52281 | 1.0673 | 0.052114 | 32.319 | 0.66
[13 empty] | 394 | 0.52198 | 1.0676 | 0.052179 | 32.352 | 0.66
[13 empty] | 395 | 0.52115 | 1.0678 | 0.052244 | 32.385 | 0.66
[13 empty] | 396 | 0.52032 | 1.068 | 0.052309 | 32.418 | 0.66
[13 empty] | 397 | 0.51949 | 1.0683 | 0.052374 | 32.451 | 0.66
[13 empty] | 398 | 0.51866 | 1.0685 | 0.05244 | 32.484 | 0.66
[13 empty] | 399 | 0.51783 | 1.0688 | 0.052505 | 32.517 | 0.66
[13 empty] | 400 | 0.517 | 1.069 | 0.05257 | 32.55 | 0.66
[13 empty] | 401 | 0.51629 | 1.0692 | 0.052631 | 32.579 | 0.66
[13 empty] | 402 | 0.51557 | 1.0695 | 0.052693 | 32.608 | 0.66
[13 empty] | 403 | 0.51486 | 1.0697 | 0.052754 | 32.637 | 0.66
[13 empty] | 404 | 0.51414 | 1.07 | 0.052816 | 32.666 | 0.66
[13 empty] | 405 | 0.51343 | 1.0702 | 0.052877 | 32.695 | 0.66
[13 empty] | 406 | 0.51272 | 1.0704 | 0.052938 | 32.724 | 0.66
[13 empty] | 407 | 0.512 | 1.0707 | 0.053 | 32.753 | 0.66
[13 empty] | 408 | 0.51129 | 1.0709 | 0.053061 | 32.782 | 0.66
[13 empty] | 409 | 0.51057 | 1.0712 | 0.053123 | 32.811 | 0.66
[13 empty] | 410 | 0.50986 | 1.0714 | 0.053184 | 32.84 | 0.66
[13 empty] | 411 | 0.50915 | 1.0716 | 0.053245 | 32.869 | 0.66
[13 empty] | 412 | 0.50843 | 1.0719 | 0.053307 | 32.898 | 0.66
[13 empty] | 413 | 0.50772 | 1.0721 | 0.053368 | 32.927 | 0.66
[13 empty] | 414 | 0.507 | 1.0724 | 0.05343 | 32.956 | 0.66
[13 empty] | 415 | 0.50629 | 1.0726 | 0.053491 | 32.985 | 0.66
[13 empty] | 416 | 0.50558 | 1.0728 | 0.053552 | 33.014 | 0.66
[13 empty] | 417 | 0.50486 | 1.0731 | 0.053614 | 33.043 | 0.66
[13 empty] | 418 | 0.50415 | 1.0733 | 0.053675 | 33.072 | 0.66
[13 empty] | 419 | 0.50343 | 1.0736 | 0.053737 | 33.101 | 0.66
[13 empty] | 420 | 0.50272 | 1.0738 | 0.053798 | 33.13 | 0.66
[13 empty] | 421 | 0.50201 | 1.074 | 0.053859 | 33.159 | 0.66
[13 empty] | 422 | 0.50129 | 1.0743 | 0.053921 | 33.188 | 0.66
[13 empty] | 423 | 0.50058 | 1.0745 | 0.053982 | 33.217 | 0.66
[13 empty] | 424 | 0.49986 | 1.0748 | 0.054044 | 33.246 | 0.66
[13 empty] | 425 | 0.49915 | 1.075 | 0.054105 | 33.275 | 0.66
[13 empty] | 426 | 0.49844 | 1.0752 | 0.054166 | 33.304 | 0.66
[13 empty] | 427 | 0.49772 | 1.0755 | 0.054228 | 33.333 | 0.66
[13 empty] | 428 | 0.49701 | 1.0757 | 0.054289 | 33.362 | 0.66
[13 empty] | 429 | 0.49629 | 1.076 | 0.054351 | 33.391 | 0.66
[13 empty] | 430 | 0.49558 | 1.0762 | 0.054412 | 33.42 | 0.66
[13 empty] | 431 | 0.49487 | 1.0764 | 0.054473 | 33.449 | 0.66
[13 empty] | 432 | 0.49415 | 1.0767 | 0.054535 | 33.478 | 0.66
[13 empty] | 433 | 0.49344 | 1.0769 | 0.054596 | 33.507 | 0.66
[13 empty] | 434 | 0.49272 | 1.0772 | 0.054658 | 33.536 | 0.66
[13 empty] | 435 | 0.49201 | 1.0774 | 0.054719 | 33.565 | 0.66
[13 empty] | 436 | 0.4913 | 1.0776 | 0.05478 | 33.594 | 0.66
[13 empty] | 437 | 0.49058 | 1.0779 | 0.054842 | 33.623 | 0.66
[13 empty] | 438 | 0.48987 | 1.0781 | 0.054903 | 33.652 | 0.66
[13 empty] | 439 | 0.48915 | 1.0784 | 0.054965 | 33.681 | 0.66
[13 empty] | 440 | 0.48844 | 1.0786 | 0.055026 | 33.71 | 0.66
[13 empty] | 441 | 0.48773 | 1.0788 | 0.055087 | 33.739 | 0.66
[13 empty] | 442 | 0.48701 | 1.0791 | 0.055149 | 33.768 | 0.66
[13 empty] | 443 | 0.4863 | 1.0793 | 0.05521 | 33.797 | 0.66
[13 empty] | 444 | 0.48558 | 1.0796 | 0.055272 | 33.826 | 0.66
[13 empty] | 445 | 0.48487 | 1.0798 | 0.055333 | 33.855 | 0.66
[13 empty] | 446 | 0.48416 | 1.08 | 0.055394 | 33.884 | 0.66
[13 empty] | 447 | 0.48344 | 1.0803 | 0.055456 | 33.913 | 0.66
[13 empty] | 448 | 0.48273 | 1.0805 | 0.055517 | 33.942 | 0.66
[13 empty] | 449 | 0.48201 | 1.0808 | 0.055579 | 33.971 | 0.66
[13 empty] | 450 | 0.4813 | 1.081 | 0.05564 | 34 | 0.66
[13 empty] | 451 | 0.48068 | 1.0812 | 0.055697 | 34.03 | 0.66
[13 empty] | 452 | 0.48006 | 1.0815 | 0.055754 | 34.06 | 0.66
[13 empty] | 453 | 0.47943 | 1.0817 | 0.05581 | 34.09 | 0.66
[13 empty] | 454 | 0.47881 | 1.082 | 0.055867 | 34.12 | 0.66
[13 empty] | 455 | 0.47819 | 1.0822 | 0.055924 | 34.15 | 0.66
[13 empty] | 456 | 0.47757 | 1.0824 | 0.055981 | 34.18 | 0.66
[13 empty] | 457 | 0.47695 | 1.0827 | 0.056038 | 34.21 | 0.66
[13 empty] | 458 | 0.47632 | 1.0829 | 0.056094 | 34.24 | 0.66
[13 empty] | 459 | 0.4757 | 1.0832 | 0.056151 | 34.27 | 0.66
[13 empty] | 460 | 0.47508 | 1.0834 | 0.056208 | 34.3 | 0.66
[13 empty] | 461 | 0.47446 | 1.0836 | 0.056265 | 34.33 | 0.66
[13 empty] | 462 | 0.47384 | 1.0839 | 0.056322 | 34.36 | 0.66
[13 empty] | 463 | 0.47321 | 1.0841 | 0.056378 | 34.39 | 0.66
[13 empty] | 464 | 0.47259 | 1.0844 | 0.056435 | 34.42 | 0.66
[13 empty] | 465 | 0.47197 | 1.0846 | 0.056492 | 34.45 | 0.66
[13 empty] | 466 | 0.47135 | 1.0848 | 0.056549 | 34.48 | 0.66
[13 empty] | 467 | 0.47073 | 1.0851 | 0.056606 | 34.51 | 0.66
[13 empty] | 468 | 0.4701 | 1.0853 | 0.056662 | 34.54 | 0.66
[13 empty] | 469 | 0.46948 | 1.0856 | 0.056719 | 34.57 | 0.66
[13 empty] | 470 | 0.46886 | 1.0858 | 0.056776 | 34.6 | 0.66
[13 empty] | 471 | 0.46824 | 1.086 | 0.056833 | 34.63 | 0.66
[13 empty] | 472 | 0.46762 | 1.0863 | 0.05689 | 34.66 | 0.66
[13 empty] | 473 | 0.46699 | 1.0865 | 0.056946 | 34.69 | 0.66
[13 empty] | 474 | 0.46637 | 1.0868 | 0.057003 | 34.72 | 0.66
[13 empty] | 475 | 0.46575 | 1.087 | 0.05706 | 34.75 | 0.66
[13 empty] | 476 | 0.46513 | 1.0872 | 0.057117 | 34.78 | 0.66
[13 empty] | 477 | 0.46451 | 1.0875 | 0.057174 | 34.81 | 0.66
[13 empty] | 478 | 0.46388 | 1.0877 | 0.05723 | 34.84 | 0.66
[13 empty] | 479 | 0.46326 | 1.088 | 0.057287 | 34.87 | 0.66
[13 empty] | 480 | 0.46264 | 1.0882 | 0.057344 | 34.9 | 0.66
[13 empty] | 481 | 0.46202 | 1.0884 | 0.057401 | 34.93 | 0.66
[13 empty] | 482 | 0.4614 | 1.0887 | 0.057458 | 34.96 | 0.66
[13 empty] | 483 | 0.46077 | 1.0889 | 0.057514 | 34.99 | 0.66
[13 empty] | 484 | 0.46015 | 1.0892 | 0.057571 | 35.02 | 0.66
[13 empty] | 485 | 0.45953 | 1.0894 | 0.057628 | 35.05 | 0.66
[13 empty] | 486 | 0.45891 | 1.0896 | 0.057685 | 35.08 | 0.66
[13 empty] | 487 | 0.45829 | 1.0899 | 0.057742 | 35.11 | 0.66
[13 empty] | 488 | 0.45766 | 1.0901 | 0.057798 | 35.14 | 0.66
[13 empty] | 489 | 0.45704 | 1.0904 | 0.057855 | 35.17 | 0.66
[13 empty] | 490 | 0.45642 | 1.0906 | 0.057912 | 35.2 | 0.66
[13 empty] | 491 | 0.4558 | 1.0908 | 0.057969 | 35.23 | 0.66
[13 empty] | 492 | 0.45518 | 1.0911 | 0.058026 | 35.26 | 0.66
[13 empty] | 493 | 0.45455 | 1.0913 | 0.058082 | 35.29 | 0.66
[13 empty] | 494 | 0.45393 | 1.0916 | 0.058139 | 35.32 | 0.66
[13 empty] | 495 | 0.45331 | 1.0918 | 0.058196 | 35.35 | 0.66
[13 empty] | 496 | 0.45269 | 1.092 | 0.058253 | 35.38 | 0.66
[13 empty] | 497 | 0.45207 | 1.0923 | 0.05831 | 35.41 | 0.66
[13 empty] | 498 | 0.45144 | 1.0925 | 0.058366 | 35.44 | 0.66
[13 empty] | 499 | 0.45082 | 1.0928 | 0.058423 | 35.47 | 0.66
[13 empty] | 500 | 0.4502 | 1.093 | 0.05848 | 35.5 | 0.66
[13 empty] | 501 | 0.44968 | 1.0932 | 0.05853 | 35.528 | 0.6601
[13 empty] | 502 | 0.44917 | 1.0935 | 0.05858 | 35.556 | 0.6602
[13 empty] | 503 | 0.44865 | 1.0937 | 0.058631 | 35.584 | 0.6603
[13 empty] | 504 | 0.44814 | 1.0939 | 0.058681 | 35.612 | 0.6604
[13 empty] | 505 | 0.44762 | 1.0941 | 0.058731 | 35.64 | 0.6605
[13 empty] | 506 | 0.4471 | 1.0944 | 0.058781 | 35.668 | 0.6606
[13 empty] | 507 | 0.44659 | 1.0946 | 0.058831 | 35.696 | 0.6607
[13 empty] | 508 | 0.44607 | 1.0948 | 0.058882 | 35.724 | 0.6608
[13 empty] | 509 | 0.44556 | 1.0951 | 0.058932 | 35.752 | 0.6609
[13 empty] | 510 | 0.44504 | 1.0953 | 0.058982 | 35.78 | 0.661
[13 empty] | 511 | 0.44452 | 1.0955 | 0.059032 | 35.808 | 0.6611
[13 empty] | 512 | 0.44401 | 1.0958 | 0.059082 | 35.836 | 0.6612
[13 empty] | 513 | 0.44349 | 1.096 | 0.059133 | 35.864 | 0.6613
[13 empty] | 514 | 0.44298 | 1.0962 | 0.059183 | 35.892 | 0.6614
[13 empty] | 515 | 0.44246 | 1.0964 | 0.059233 | 35.92 | 0.6615
[13 empty] | 516 | 0.44194 | 1.0967 | 0.059283 | 35.948 | 0.6616
[13 empty] | 517 | 0.44143 | 1.0969 | 0.059333 | 35.976 | 0.6617
[13 empty] | 518 | 0.44091 | 1.0971 | 0.059384 | 36.004 | 0.6618
[13 empty] | 519 | 0.4404 | 1.0974 | 0.059434 | 36.032 | 0.6619
[13 empty] | 520 | 0.43988 | 1.0976 | 0.059484 | 36.06 | 0.662
[13 empty] | 521 | 0.43936 | 1.0978 | 0.059534 | 36.088 | 0.6621
[13 empty] | 522 | 0.43885 | 1.0981 | 0.059584 | 36.116 | 0.6622
[13 empty] | 523 | 0.43833 | 1.0983 | 0.059635 | 36.144 | 0.6623
[13 empty] | 524 | 0.43782 | 1.0985 | 0.059685 | 36.172 | 0.6624
[13 empty] | 525 | 0.4373 | 1.0987 | 0.059735 | 36.2 | 0.6625
[13 empty] | 526 | 0.43678 | 1.099 | 0.059785 | 36.228 | 0.6626
[13 empty] | 527 | 0.43627 | 1.0992 | 0.059835 | 36.256 | 0.6627
[13 empty] | 528 | 0.43575 | 1.0994 | 0.059886 | 36.284 | 0.6628
[13 empty] | 529 | 0.43524 | 1.0997 | 0.059936 | 36.312 | 0.6629
[13 empty] | 530 | 0.43472 | 1.0999 | 0.059986 | 36.34 | 0.663
[13 empty] | 531 | 0.4342 | 1.1001 | 0.060036 | 36.368 | 0.6631
[13 empty] | 532 | 0.43369 | 1.1004 | 0.060086 | 36.396 | 0.6632
[13 empty] | 533 | 0.43317 | 1.1006 | 0.060137 | 36.424 | 0.6633
[13 empty] | 534 | 0.43266 | 1.1008 | 0.060187 | 36.452 | 0.6634
[13 empty] | 535 | 0.43214 | 1.1011 | 0.060237 | 36.48 | 0.6635
[13 empty] | 536 | 0.43162 | 1.1013 | 0.060287 | 36.508 | 0.6636
[13 empty] | 537 | 0.43111 | 1.1015 | 0.060337 | 36.536 | 0.6637
[13 empty] | 538 | 0.43059 | 1.1017 | 0.060388 | 36.564 | 0.6638
[13 empty] | 539 | 0.43008 | 1.102 | 0.060438 | 36.592 | 0.6639
[13 empty] | 540 | 0.42956 | 1.1022 | 0.060488 | 36.62 | 0.664
[13 empty] | 541 | 0.42904 | 1.1024 | 0.060538 | 36.648 | 0.6641
[13 empty] | 542 | 0.42853 | 1.1027 | 0.060588 | 36.676 | 0.6642
[13 empty] | 543 | 0.42801 | 1.1029 | 0.060639 | 36.704 | 0.6643
[13 empty] | 544 | 0.4275 | 1.1031 | 0.060689 | 36.732 | 0.6644
[13 empty] | 545 | 0.42698 | 1.1034 | 0.060739 | 36.76 | 0.6645
[13 empty] | 546 | 0.42646 | 1.1036 | 0.060789 | 36.788 | 0.6646
[13 empty] | 547 | 0.42595 | 1.1038 | 0.060839 | 36.816 | 0.6647
[13 empty] | 548 | 0.42543 | 1.104 | 0.06089 | 36.844 | 0.6648
[13 empty] | 549 | 0.42492 | 1.1043 | 0.06094 | 36.872 | 0.6649
[13 empty] | 550 | 0.4244 | 1.1045 | 0.06099 | 36.9 | 0.665
[13 empty] | 551 | 0.42388 | 1.1047 | 0.06104 | 36.928 | 0.6651
[13 empty] | 552 | 0.42337 | 1.105 | 0.06109 | 36.956 | 0.6652
[13 empty] | 553 | 0.42285 | 1.1052 | 0.061141 | 36.984 | 0.6653
[13 empty] | 554 | 0.42234 | 1.1054 | 0.061191 | 37.012 | 0.6654
[13 empty] | 555 | 0.42182 | 1.1057 | 0.061241 | 37.04 | 0.6655
[13 empty] | 556 | 0.4213 | 1.1059 | 0.061291 | 37.068 | 0.6656
[13 empty] | 557 | 0.42079 | 1.1061 | 0.061341 | 37.096 | 0.6657
[13 empty] | 558 | 0.42027 | 1.1063 | 0.061392 | 37.124 | 0.6658
[13 empty] | 559 | 0.41976 | 1.1066 | 0.061442 | 37.152 | 0.6659
[13 empty] | 560 | 0.41924 | 1.1068 | 0.061492 | 37.18 | 0.666
[13 empty] | 561 | 0.41872 | 1.107 | 0.061542 | 37.208 | 0.6661
[13 empty] | 562 | 0.41821 | 1.1073 | 0.061592 | 37.236 | 0.6662
[13 empty] | 563 | 0.41769 | 1.1075 | 0.061643 | 37.264 | 0.6663
[13 empty] | 564 | 0.41718 | 1.1077 | 0.061693 | 37.292 | 0.6664
[13 empty] | 565 | 0.41666 | 1.1079 | 0.061743 | 37.32 | 0.6665
[13 empty] | 566 | 0.41614 | 1.1082 | 0.061793 | 37.348 | 0.6666
[13 empty] | 567 | 0.41563 | 1.1084 | 0.061843 | 37.376 | 0.6667
[13 empty] | 568 | 0.41511 | 1.1086 | 0.061894 | 37.404 | 0.6668
[13 empty] | 569 | 0.4146 | 1.1089 | 0.061944 | 37.432 | 0.6669
[13 empty] | 570 | 0.41408 | 1.1091 | 0.061994 | 37.46 | 0.667
[13 empty] | 571 | 0.41356 | 1.1093 | 0.062044 | 37.488 | 0.6671
[13 empty] | 572 | 0.41305 | 1.1096 | 0.062094 | 37.516 | 0.6672
[13 empty] | 573 | 0.41253 | 1.1098 | 0.062145 | 37.544 | 0.6673
[13 empty] | 574 | 0.41202 | 1.11 | 0.062195 | 37.572 | 0.6674
[13 empty] | 575 | 0.4115 | 1.1103 | 0.062245 | 37.6 | 0.6675
[13 empty] | 576 | 0.41098 | 1.1105 | 0.062295 | 37.628 | 0.6676
[13 empty] | 577 | 0.41047 | 1.1107 | 0.062345 | 37.656 | 0.6677
[13 empty] | 578 | 0.40995 | 1.1109 | 0.062396 | 37.684 | 0.6678
[13 empty] | 579 | 0.40944 | 1.1112 | 0.062446 | 37.712 | 0.6679
[13 empty] | 580 | 0.40892 | 1.1114 | 0.062496 | 37.74 | 0.668
[13 empty] | 581 | 0.4084 | 1.1116 | 0.062546 | 37.768 | 0.6681
[13 empty] | 582 | 0.40789 | 1.1119 | 0.062596 | 37.796 | 0.6682
[13 empty] | 583 | 0.40737 | 1.1121 | 0.062647 | 37.824 | 0.6683
[13 empty] | 584 | 0.40686 | 1.1123 | 0.062697 | 37.852 | 0.6684
[13 empty] | 585 | 0.40634 | 1.1126 | 0.062747 | 37.88 | 0.6685
[13 empty] | 586 | 0.40582 | 1.1128 | 0.062797 | 37.908 | 0.6686
[13 empty] | 587 | 0.40531 | 1.113 | 0.062847 | 37.936 | 0.6687
[13 empty] | 588 | 0.40479 | 1.1132 | 0.062898 | 37.964 | 0.6688
[13 empty] | 589 | 0.40428 | 1.1135 | 0.062948 | 37.992 | 0.6689
[13 empty] | 590 | 0.40376 | 1.1137 | 0.062998 | 38.02 | 0.669
[13 empty] | 591 | 0.40324 | 1.1139 | 0.063048 | 38.048 | 0.6691
[13 empty] | 592 | 0.40273 | 1.1142 | 0.063098 | 38.076 | 0.6692
[13 empty] | 593 | 0.40221 | 1.1144 | 0.063149 | 38.104 | 0.6693
[13 empty] | 594 | 0.4017 | 1.1146 | 0.063199 | 38.132 | 0.6694
[13 empty] | 595 | 0.40118 | 1.1149 | 0.063249 | 38.16 | 0.6695
[13 empty] | 596 | 0.40066 | 1.1151 | 0.063299 | 38.188 | 0.6696
[13 empty] | 597 | 0.40015 | 1.1153 | 0.063349 | 38.216 | 0.6697
[13 empty] | 598 | 0.39963 | 1.1155 | 0.0634 | 38.244 | 0.6698
[13 empty] | 599 | 0.39912 | 1.1158 | 0.06345 | 38.272 | 0.6699
[13 empty] | 600 | 0.3986 | 1.116 | 0.0635 | 38.3 | 0.67
[13 empty] | 610 | 0.3955 | 1.117 | 0.063797 | 38.399 | 0.67
[13 empty] | 620 | 0.3924 | 1.118 | 0.064094 | 38.498 | 0.67
[13 empty] | 630 | 0.3892 | 1.119 | 0.0644 | 38.6 | 0.67
[13 empty] | 640 | 0.3837 | 1.1225 | 0.06505 | 38.85 | 0.67
[13 empty] | 650 | 0.3782 | 1.126 | 0.0657 | 39.1 | 0.68
[13 empty] | 660 | 0.3741 | 1.128 | 0.06605 | 39.4 | 0.68
[13 empty] | 670 | 0.37 | 1.13 | 0.0664 | 39.7 | 0.68
[13 empty] | 680 | 0.36594 | 1.1323 | 0.066862 | 40.0861 | 0.68
[13 empty] | 690 | 0.36188 | 1.1346 | 0.067324 | 40.4722 | 0.68
[13 empty] | 700 | 0.3577 | 1.137 | 0.0678 | 40.87 | 0.69
[13 empty] | 720 | 0.35135 | 1.1405 | 0.0685 | 41.385 | 0.69
[13 empty] | 740 | 0.345 | 1.144 | 0.0692 | 41.9 | 0.69
[13 empty] | 760 | 0.33817 | 1.1476 | 0.069893 | 42.3686 | 0.69
[13 empty] | 780 | 0.33134 | 1.1513 | 0.070586 | 42.8372 | 0.7
[13 empty] | 800 | 0.3243 | 1.155 | 0.0713 | 43.32 | 0.7
[13 empty] | 825 | 0.31665 | 1.159 | 0.07205 | 43.9 | 0.7
[13 empty] | 850 | 0.309 | 1.163 | 0.0728 | 44.48 | 0.71
[13 empty] | 875 | 0.297 | 1.167 | 0.0735 | 45.57 | 0.715
[13 empty] | 900 | 0.2934 | 1.171 | 0.0743 | 45.65 | 0.72
[13 empty] | 950 | 0.2834 | 1.178 | 0.0755 | 46.76 | 0.73
[13 empty] | 1000 | 0.2734 | 1.185 | 0.0768 | 47.88 | 0.74
[13 empty] | 1100 | 0.25 | 1.2 | 0.09 | 52 | 0.705
[13 empty] | 1200 | 0.235 | 1.22 | 0.095 | 55 | 0.69